## Slide 1: ⚡ Grid Stability Prediction using Machine Learning
Transient Stability Assessment & Critical Clearing Time Estimation
on the IEEE 39-Bus New England Test System
Department of Electrical Engineering
National Institute of Technology (NIT), Raipur
Prepared By (7th Semester Minor Project):
• Sanskar Gupta (Roll No: 23117091)
• Daksh Tripathi (Roll No: 23117036)
• Karandeep Taram (Roll No: 23117052)
• Veena Gupta (Roll No: 23117112)

## Slide 2: Problem Formulation & Real-World Motivation
Transient Rotor Angle Stability:
  Severe disturbances (faults, line trips) cause synchronous generators to swing.
  Large angular separations result in pole slips, protective relay cascading, and massive blackouts.
Traditional Time-Domain Simulation (TDS):
  Solves high-dimensional non-linear DAEs: dx/dt = f(x, y, u), 0 = g(x, y, u).
  Numerically exact, but computationally slow (takes 15-30s per scenario).
  Incompatible with real-time online Dynamic Security Assessment (DSA).
Machine Learning Objective:
  Instantaneous millisecond inference directly mapping post-fault telemetry to stability outcomes.
NIT RAIPUR • EE MINOR PROJECT

## Slide 3: Central Research Question: Beyond Random Splits
The Standard Literature Flaw:
  Almost all academic publications benchmark on random 80/20 train/test splits.
  Random splits leak identical topologies and operating conditions into the test set.
  Generates a dangerous 'false sense of near-100% security'.
Our Central Research Question:
  Can an ML model trained on one set of operating conditions and disturbances generalize to unseen fault buses, extreme load levels, and N-1 contingencies?
Domain Generalization Framework:
  We reject random splits and evaluate deliberate out-of-distribution (OOD) topological and operational shifts.
NIT RAIPUR • EE MINOR PROJECT

## Slide 4: System Architecture & Simulation Engine
Test Benchmark: IEEE 39-Bus New England System
  10 Synchronous Machines (GENROU 6th-order models with IEEE-T1 exciters).
  39 Buses, 46 Transmission Lines / Transformers, 19 PQ Loads.
Simulation Engine: ANDES (Python-native DAE Solver)
  Open-source, pip-installable, license-free, 100% reproducible.
Multi-Processing Dataset Generation Harness:
  450 scenarios simulated in parallel using ProcessPoolExecutor.
  Fault clearing time: 0.05s to 0.30s.
  System load scaling: 80% to 120% nominal.
  N-1 Transmission Line Contingencies: Line 2-3, Line 16-17.
NIT RAIPUR • EE MINOR PROJECT

## Slide 5: Ground Truth Stability Labeling: COI 180° Rule
Center of Inertia (COI) Reference Frame:
  Generator rotor angles naturally swing together; evaluating absolute angle is insufficient.
  COI angle: δ_COI(t) = (Σ H_i * δ_i(t)) / (Σ H_i).
Binary Classification Ground Truth:
  UNSTABLE (0): If maximum generator deviation from COI exceeds 180 degrees during transient window (t in [0, 20s]), or numerical divergence occurs.
  STABLE (1): If all machines remain synchronized within 180 degrees of the COI.
Class Distribution:
  308 Stable cases (68.4%) vs 142 Unstable cases (31.6%).
  Achieved a highly realistic natural 2:1 imbalance.
NIT RAIPUR • EE MINOR PROJECT

## Slide 6: EDA: Physical Validation of Simulation Data
NIT RAIPUR • EE MINOR PROJECT
Physical Validation Confirmed: Longer fault clearing times drastically increase the probability of system instability.
Faults cleared under 0.10s are 100% stable; faults lingering to 0.30s destabilize the grid.

## Slide 7: Baseline Models: Standard Random Split (The Illusion)
NIT RAIPUR • EE MINOR PROJECT
In-Distribution Evaluation: Logistic Regression (100%), Random Forest (100%), XGBoost (98.9%), MLP (100%).
Under standard random splits, models achieve near-perfection with zero missed instabilities.

## Slide 8: The Core Contribution: The Generalization Gap
NIT RAIPUR • EE MINOR PROJECT
Out-of-Distribution Benchmarking Across 3 Held-Out Splits:
1. Held-Out Buses: RF accuracy drops on unseen Bus 39. MLP achieves 98.33% accuracy.
2. Held-Out Heavy Loads: XGBoost collapses to 63.89% (tree step saturation); MLP maintains 97.78% (smooth extrapolation).
3. Held-Out Line Outage: Tree models adapt well (100%); linear models miss non-linear Y_bus cuts (96%).

## Slide 9: Critical Reliability Metric: Missed Instability Rate
NIT RAIPUR • EE MINOR PROJECT
Power System Operational Risk: Predicting Unstable as Stable leads to catastrophic blackouts.
Random Forest missed 15.2% of instabilities on unseen buses without physics features.
Physics-Informed Invariant Features reduced this failure rate by more than half (down to 7.1%).

## Slide 10: Critical Clearing Time (CCT) ML Regression
NIT RAIPUR • EE MINOR PROJECT
Ground-Truth from ANDES Bisection Search across 45 operating conditions.
ML Regressor achieves R² = 0.9636 and RMSE = 25 milliseconds (under 1.5 electrical cycles).
Enables continuous dynamic security margins rather than just binary labels.

## Slide 11: Headline Finding: >33,000x Operational Speedup
NIT RAIPUR • EE MINOR PROJECT
Numerical ANDES Bisection Search: 23.88 seconds per operating condition.
Machine Learning Inference: 0.70 milliseconds (XGBoost) / 0.04 milliseconds (Ridge).
Speedup Factor: >33,000x faster — transforming offline simulation into real-time online DSA.

## Slide 12: Model Explainability via TreeSHAP
NIT RAIPUR • EE MINOR PROJECT
Physics Verification via Cooperative Game Theory:
1. v_mean_system (|SHAP|=3.75) and v_min_system dominate predictions.
2. Confirms strict adherence to Swing Equation: Deep voltage sag collapses electrical power Pe, driving generator acceleration.

## Slide 13: Local Explainability: Stable vs Unstable Case Studies
NIT RAIPUR • EE MINOR PROJECT
Individual Scenario Attribution: Decomposes exact contribution of clearing time, voltage sag, and bus location.
Provides human transmission operators with actionable reasoning before executing remedial action.

## Slide 14: Interactive Digital Twin Web Application
Streamlit Interactive Dashboard (`app/streamlit_app.py`):
  Real-time reactive prediction interface running at localhost:8501.
Core Dashboard Features:
  Dynamic Scenario Sliders: Fault Bus, Load Scale (0.8x-1.3x), Clearing Time (0.04s-0.40s).
  Real-Time Stability Gauge: Instant STABLE (Green) vs UNSTABLE POLE SLIP (Red).
  Dynamic CCT Safety Margin Meter: Displays safety margin (t_cct - t_clear in ms).
  Live SHAP Waterfall Attribution: Real-time decomposition of contributing risk factors.
  Pre-canned Scenarios: Safe Nominal, High-Stress Staged Fault, Generator Terminal Fault.
NIT RAIPUR • EE MINOR PROJECT

## Slide 15: Engineering Rigor: Architecture Decision Records
Formally Documented 7 ADRs (`docs/adr/`):
  ADR-0001: ANDES Simulator & IEEE 39-Bus Benchmark Selection
  ADR-0002: Ground Truth Labeling via COI 180° Rotor Deviation Rule
  ADR-0003: Domain Generalization Protocol (Rejecting Random Train/Test Splits)
  ADR-0004: Neural Network (MLP) Convergence & Stress Extrapolation Analysis
  ADR-0005: Physics-Informed Invariant Feature Engineering (Equal Area Criterion)
  ADR-0006: TreeSHAP Interpretability & Swing Equation Physical Validation
  ADR-0007: CCT Bisection Search Ground Truth & >33,000x Speedup Benchmark
NIT RAIPUR • EE MINOR PROJECT

## Slide 16: Conclusion & 8th Semester Continuation Plan
Minor Project Wrap-up Summary:
  Built end-to-end simulation, dataset, ML classification, CCT regression, XAI, and web demo.
  Answered Central Research Question: Proved why standard ML collapses under domain shift and how physics features mitigate it.
  Delivered 33,000x inference speedup for online Dynamic Security Assessment.
Major Project (8th Semester Continuation Roadmap):
  Spatio-temporal Graph Neural Networks (GNNs) incorporating the bus admittance matrix Y_bus directly.
  Self-supervised World Models (JEPA) pre-trained on multi-channel Phasor Measurement Unit (PMU) time-series streams.
  Active remedial control action integration (emergency load shedding, fast battery response).
NIT RAIPUR • EE MINOR PROJECT